
WATERWORKS EMERGENCY PLAN

Valley Ridge Community Cooperative
Date Completed: Nov 20,2012
Date Approved By Waterworks Board: Nov 27,2012
Date Revised by Waterworks Board: Mar 02, 2014

Date Revised by Waterworks Board: Dec 2, 2020

Section 1 – Introduction and Policy Statement

The intent of this emergency plan is to ensure the safety of consumers and the protection of life, property and the environment in the most efficient way possible in the event of an unexpected incident.  In particular, this plan deals with events that may affect water quality.

The performance goals and acceptable levels of service are outlined below.  

Goal 1: Life Safety

The primary goal of the water system is to ensure the safety of its residents.  At all times, safe, clean water should be provided to the public.  

Examples of conditions that should never occur are the failure of the distribution system; the distribution of contaminated water; the release of hazardous materials; and the collapse of structures.

	Section 2 - Emergency Response Contact List 
	
	 

	Waterworks Name
	Valley Ridge Community Cooperative 

	
	
	
	
	

	Source Water
	 Buffalo Pound WTP via City of Moose Jaw
 
	 
	 

	
	
	 
	 

	 
	 
	 
	 
	 

	PERSONNEL CONTACT  PHONE / FAX NUMBERS
	 
	 
	 

	 
	 
	PHONE
	 

	CONTACT NAME
	 
	HOME 
	CELL
	Email

	 
	 
	 
	 
	 

	Operator’s Name
	Jamie Tatum
	
	306-631-5011 
	Jamie.tatum@hotmail.com 

	President of Board
	Nicole Seefried
	
	306-513-7287 
	Nicole.seefried@mosaicco.com 

	Board Member 
	Donna Hoffman
	
	306-533-5006 
	Donna.hoffman@sasktel.net 

	
	Jodi Sims
	
	306-631-7653
	jodisims@sasktel.net 

	 
	 
	 
	 
	 

	EMERGENCY CONTACT NUMBERS
	 
	 
	 

	 
	 
	PHONE
	 

	CONTACT NAME
	 
	WORK 
	CELL
	Email

	Sask Health, Moose Jaw Office
	Ask for PHI on call
	306-691-1500 
	
	

	Water Security Agency
Environmental Project Officer
	Andrew Hickey
	       
	306-630-3683 
	

	Water Security Agency 24hr Upset Report                        
	
	1-844-536-9494
	
	

	Saskatchewan Emergency Management Organization (EMO) 24 Hour Line – 7 Days a Week
	Regina
	306-787-9563
	 
	 

	
	
	
	
	 

	SE Spill Emergency Number (For Spills Only)
	
	1-800-667-7525
	 
	 

	Police
	911
	 306-694-7600
	 
	 

	Ambulance
	 
	 911
	 
	 

	Fire Department
	 
	 911
	 
	 

	Municipal Engineer
	 
	 
	 
	 

	Pump Manufacturer
	Clark’s Supply 
	306-693-4334 
	 
	 

	Chlorinator Manufacturer
	 
	N/A 
	 
	 

	Chemical Supplier
	ClearTech 
	 306-664-2522
	
	

	Excavation Services
	 
	 
	 
	 

	Electrician
	Pro-Tec Electric 
	306-693-7733
	
	

	Plumbing Services
	 
	 
	 
	 

	Bulk Water Hauler
	Oasis on Wheels 
	306-693-7481 
	 
	 

	Bottled Water Supplier
	Culligan
	306-693-0606
	
	


	

	UTILITY CONTACT NUMBERS 

	 
	
	PHONE
 

	CONTACT NAME
	
	
	
	

	Sask Power
	Emergency Contact
	306-310-2220

	Sask Power
	General Inquiries
	1-888-757-6937

	Sask Tel
	Repair Service and Locate
	1-866-828-4888

	Transgas
	Emergency
	306-777-9800

	Sask Energy
	Emergency
	1-888-700-0427

	Sask Energy
	Line Locate
	1-866-828-4888

	CP Railways
	
	1-800-795-7851`

	CN Railways
	
	

	SaskWater
	MJ Head Office
	1-888-230-1111


Section 3 - Organizational Responsibilities

Waterworks Emergency Planning and Crisis Management Task Force Members

Water Quality Crisis Coordinator

Public Relations Coordinator

President – Nicole Seefried
Cell # 306-513-7287
Water Security Agency
Andrew Hickey, Environment Project Officer

111-101 Fairford St. East Moose Jaw SK, S6H 7X9
Cell - 306-630 3683
Saskatchewan Health Authority – Moose Jaw Office
1000B Albert St
Moose Jaw SK
Phone: 306-691-2300

Section 4 - Notification and Communication

Emergency Notification to Customer   

The system notifies all system users via the following manner in case of an emergency:
  (  Phone calls and/or email depending on time sensitivity of the emergency. All residents have contact list with phone/email for all residents. 
Signs

All example signs (Precautionary Drinking Water Advisory & Emergency Boil Water Order) are available from Water Security Agency document entitled “Adverse Drinking Water Quality Incident and Bacteriological Follow-Up Standard, November 2019, EPB 505”
[image: image1.png]()

Water Security
Agency

Precautionary Drinking Water Advisory

This Advisory applies to users on the Valley Ridge Community Co-op water works system, and is
effective at 10:00 am. on Wednesday November 04, 2020.

Pursuantto clause 36(1)(a) of The Environmental Management and Protection Act, 2010 this
Precautionary Drinking Water Advisory is issued due to works on the system cansing a
depressurizafion,as a result the safety of the CO-OP's drinking water supply cannot be ensured af all
times. Therefore, pursuant to Clause 36(1)(b) of The Emvironmental Management and Protection
Act, 2010, consumers must be notified to

@
®

@©
@

Boil all water, used for drinking purposes, for at least one (1) minutes, at a rolling boil, prior
tousage,

Boil water to be used for other activities where it may be ingested, including

()  brushing teeth or soaking false tecth;

(i)  washing fruits and vegetables;

(iii)  food or drink which will not be subsequently heated; and

(i) ice cubes;

Mot drink from any public drinking fountains supplied with water from the public water
supply;

Under most circumstances, no need to boil water used for other household purposes, such as
Laundry. Adults, adolescents and ol der children may shower, bathe or wash using tap water
but should avoid swallowing the water. Dishes may be disinfected by washing in dishwashing
machines that have a dry cycle or afinal rinse that excesds 45°C for 20 minutes, 50°C for 5
minutes, or 72°C for 1 minute;

Ensure that younger children and infants are sponge bathed,

Use an alternativ e water source known to be safe, if they do not wish to boil the water, and
Consult with your physician if you have cuts or rashes that are severe before using the water.

If you require any additional information, please contact the foll owing:

CO-OP Contact (306) 513-7287
Water Security Agency (306) 6303683
Saskatchewan Health Authority-Moose Jaw (306) 691-1500




Section 5 - Technical Action Plans

Many emergency situations can lead to water quality degradation, for example, a main break, a power outage, pumping equipment failure, or a natural disaster.  Other emergency situations are a direct result of a water quality problem, such as a waterborne disease outbreak, bacterial contamination of the distribution system or contamination of the source of supply.  Water service can be disrupted by these events, and water quality can be threatened if not degraded.

1) Flood Conditions

Trigger Events: Widespread flooding occurs.

(Disaster)

Actions: 

· Notify Water Security Agency – Environmental Project Officer

· Notify users of the potential for water contamination, loss of pressure, power, etc.  Users should be advised to store some drinking water in advance and to boil any suspect water for one minute.

· Contact local media for public service announcement (where all customers can not be notified by phone)

· Contact government agencies (see below) for advice and assistance

Contacts:

· Board Members, Water Security Agency (Local Environmental Project Officer), Saskatchewan Emergency Planning, and others as necessary.

2) Outbreak of a Waterborne Disease

Trigger Events:  Local Health District notifies the water system of a confirmed outbreak.

(Major emergency to disaster)

Actions: 

· Notify Water Security Agency – Environmental Project Officer

· Notify users of the potential for water contamination.  Users should be advised to boil any suspect water for one minute.

· Contact government agencies (see below) for advice and assistance

Contacts:

· Board members, Water Security Agency (Local Environmental Project Officer), Saskatchewan Emergency Planning, and others as necessary.
3) Microbial Contamination Detected

Trigger event: A positive microbial test result is received for the treated water.

(Routine incident to major emergency)

Actions: 

· Follow Saskatchewan’s Bacteriological Follow-up Procedures document.

Contacts:

· As per Saskatchewan’s Bacteriological Follow-up Procedures document.

4) Distribution System Problems

a) Significant loss of pressure in the system

Trigger Events: Potential Backflow throughout the distribution system

(Major Emergency)

Actions: 

· Notify Water Security Agency – Environmental Project Officer

· Notify users of to boil their water for one minute or take other disinfection procedures or as instructed by Water Security Agency
· Purge and disinfect lines as directed

Contacts:

· Owners of water system, Water Security Agency (Local Environmental Project Officer)

b) Water Breaks - Sanitary Repair Procedures

Trigger Event: Main Line Breaks 

(Major Emergency)

Repairing a main break is the most common type of emergency maintenance in a distribution system. Depending on site-specific conditions, a main break may be a source of contamination. For example, if the damaged pipe is below the water table or in contact with a sewage or storm water main, contamination may occur.  As noted below, maintenance procedures differ for main breaks between those breaks likely and unlikely to cause contamination.  Contact your local Environmental Project Officer if you are unsure about whether contamination is expected for a particular break.

If contamination is not expected, 

Actions:

· Call excavation contractor

· Treat the replacement pipe and fittings with a chlorine solution.

· Notify downstream users of interruption of water service, if required

Contacts:

· Owners of the water system, excavation contractor and others as necessary

If the existing main is partially or wholly dewatered, some of the following steps may be necessary to repair the main:

Actions (AWWA C651-99):

· Control water loss by completely or partially shutting down the main.

· Flushing may be used to minimize flow toward the damaged main, thus reducing the extent of possible contamination. 

· Water should be reduced to a level below the break as quickly as possible. Groundwater may be treated with hypochlorite while repairs are underway. If the water appears to be clear, a 25 to 50 ppm dose may be sufficient. If sewage is present, a dose greater than 100 ppm is suggested.

· Customers at higher elevations than the break should be notified to shut off the inlet valve at their meter to prevent siphoning of hot-water tanks or softeners. 

· Extensive flushing may be used to purge possible contaminants and to bring clear water to the point of damage. 

· Chlorine residuals should be checked hourly to evaluate the effectiveness of pumping and flushing procedures. 
· Mains which have been repaired after a break or leak need to be cleaned, disinfected and monitored before being returned to service.  

· Monitoring that follows a main disinfection or the addition of a new facility usually entails a check for microbial activity and disinfectant residuals.

Contacts:

· Owners of water system, Water Security Agency (Local Environmental Project Officer), excavation contractor and others as necessary.
 

5) Customer Complaints 

Trigger Event: Consumer complaint

(Routine Incident)

Water quality complaints should be logged in a retrievable format for tracking and reporting purposes.  Tracking the complaints can help identify problem areas of the system.  Temporary fixes (such as flushing) should not be used to address chronic water quality problems (such as excessive chlorine demand, turbidity, sediment, corrosive water, etc.).  

Actions:

· Log the water quality complaint

· Investigate the water quality complaint

Contacts:

· None

PAGE  

